Attachment I: Design Description of China-aid Georgia Mental Health Hospital

Design basis: the relevant codes of architectural design of the People’s Republic of China, as well as mandatory regulations and customary practices of Georgia.

The Project includes Telavi Project and Senaki Project. If the contents of this Description are not indicated, it means that the said contents are applicable to both Telavi and Senaki projects.

1	Architectural Design Description

1.1	Project Overview

Telavi City

Project Name: Mental Health Hospital of Telavi City, Georgia

Construction site: the northern suburb of Telavi City, Georgia, with a total construction land area of about 6227 m2.

Status of the site: The land is an open space not built in the suburbs, and a municipal highway is on the west side. The land is basically flat and there are no buildings to be demolished on the ground.

Project scale: The total construction area is 2264 m2.

Project function: outpatient building, ward building, equipment room and ancillary facilities.

Senaki City

Project Name: Mental Health Hospital of Senaki in Georgia

Construction site: the former mental health hospital in eastern Senaki City, Georgia, with a total construction land area of 4330 m2.

Site status: The land is in the former mental health hospital. The northeast side of the land is connected with the external roads. The site is basically flat. There are two old buildings abandoned by the former hospital on the ground.

Project scale: The total construction area is 2230 m2.

Project function: outpatient building, ward building, equipment room and ancillary facilities.

1.2	General Plan Design

Telavi City

The land is relatively square. The main entrance is located on the west side. Three buildings are arranged in a C-shape. The outpatient building is located on the west side directly facing the main entrance, and the ward building is located on the south side; the above two buildings are connected by corridors. The equipment room is located on the north side. The rehabilitation garden is located in the center of the land.

Senaki City

The land is irregularly elongated. The main entrance is located on the northeast side, and the equipment room is located on the north side. The middle clinic building is directly facing the external connection road. The ward building is located on the south side. The outpatient building and the ward building are connected by corridors.

1.3	Road Traffic

Telavi City

The main entrance of the Project is on the west side. There are two entrances to the hospital area. A traffic loop is set up in the area. The outpatient building and ward building are set up in the loop. Parking spaces are set up on the west and north sides of the loop.

Senaki City

The main entrance of the Project is on the northeast side. A traffic loop is set up in the area. The outpatient building and ward building are set up in the loop. Parking spaces are set up on the south side of the loop.

1.4	Building Design

TelaviCity

The architecture is simple and lively in style, and the roof and facade are designed with local architectural features. In terms of plane design, it is characterized by simplicity, practicality and high efficiency, meeting the functional and usage requirements of local medical buildings, and the internal streamline and functional relationship of outpatient building and ward building are reasonable. Building lighting and ventilation adapt to local climate characteristics.

Senaki City

The architecture is simple and lively in style, and the roof and facade are designed with local architectural features. In terms of plane design, it is characterized by simplicity, practicality and high efficiency, meeting the functional and usage requirements of local medical buildings, and the internal streamline and functional relationship of outpatient building and ward building are reasonable. Building lighting and ventilation adapt to local climate characteristics.

1.5	Medical Technology

Telavi City

The Project is a mental health hospital with 30 beds for in-patient treatment. The main functions include outpatient department (including registration, consultation room, drug storage, injection treatment and other rooms), crisis intervention department (including registration, disposal, treatment and other rooms), psychological rehabilitation service department (including registration, various rehabilitation treatments, kitchen, restaurant and other rooms), 30-bed inpatient department, logistics office department and equipment room.

The Project is mainly provided with medical equipment, including basic electrocardiograph, dynamic electroencephalograph, brain function diagnosis and treatment instrument and other mobile inspection equipment.

Senaki City

The Project is a mental health hospital with 30 beds for in-patient treatment. The main functions include outpatient department (including registration, consultation room, drug storage, injection treatment and other rooms), crisis intervention department (including registration, disposal, treatment and other rooms), psychological rehabilitation service department (including registration, various rehabilitation treatments, kitchen, restaurant and other rooms), 30-bed inpatient department, logistics office department and equipment room.

The Project is mainly provided with medical equipment, including basic B-ultrasound, electrocardiogram, dynamic electroencephalograph, brain function diagnosis and treatment instrument, sleep electroencephalograph analyzer, inspection equipment and other mobile inspection equipment.

1.6	Main Technical and Economic Indicators

Telavi City

| S/N | Name |  | Unit | Qty. |
| --- | --- | --- | --- | --- |
| 1 | Total land area |  | m2 | 6227 |
| 2 | Gross floor area |  | m2 | 2262 |
|  | Including | Outpatient building |  | 745 |
|  |  | Inpatient building |  | 1368 |
|  |  | Equipment room |  | 138 |
|  |  | Guard room and others |  | 11 |
| 3 | Floor area ratio |  |  | 0.35 |
| 4 | Greening rate |  | % | 45 |
| 5 | Building height |  | m | 12.6 |
| 6 | Building stories |  | Floor | 1-3 |
| 7 | Building area |  | m2 | 989 |
| 8 | Building density |  | % | 15.5 |
| 9 | Number of sickbeds |  | Nos. | 30 |
| 10 | Parking number of motor vehicle |  | Nos. | 17 |

Senaki City

| S/N | Name |  | Unit | Qty. |
| --- | --- | --- | --- | --- |
| 1 | Total land area |  | m2 | 4330 |
| 2 | Gross floor area |  | m2 | 2230 |
|  | Including | Outpatient building |  | 745 |
|  |  | Inpatient building |  | 1334 |
|  |  | Equipment room |  | 138 |
|  |  | Guard room and others |  | 11 |
| 3 | Floor area ratio |  |  | 0.51 |
| 4 | Greening rate |  | % | 38 |
| 5 | Building height |  | m | 12.6 |
| 6 | Building stories |  | Floor | 1-3 |
| 7 | Building area |  | m2 | 967 |
| 8 | Building density |  | % | 22 |
| 9 | Number of sickbeds |  | Nos. | 30 |
| 10 | Parking number of motor vehicle |  | Nos. | 10 |

2	Structural Design Description

2.1	Structural Safety Grade: Grade II;

Design service life of the structure: 50 years

2.2	Natural Conditions and Seismic Fortification Intensity

Basic wind pressure:    kPa;

Basic snow pressure: 0.50kpa in Telavi; 0.50kpa in Senaki.

Permafrost depth: 0m in Telavi; 0m in Senaki.

Seismic fortification intensity: 9 degrees in Telavi; 8 degrees in Senaki.

Earthquake acceleration: 0.32g in Telavi; 0.17g in Senaki.

2.3	Main Structural Materials

2.3.1	Concrete strength grade: Cushion C15; the concrete strength grade of the main structure: C25~C30.

2.3.2	Masonry materials: Fired perforated brick; concrete hollow brick; mortar strength: M5.0.

2.3.3	The reinforcement shall be of HRB400 grade and shall conform to the current Chinese national standard Hot Rolled Ribbed Steel Bars for the Reinforcement of Concrete (GB1499).

2.3.4	Q345GJCZ15 and Q345GJCZ25 steels shall be used, and they shall also be qualified for tensile strength, elongation, yield strength, carbon, sulfur, phosphorus content and cold bending test. The ratio between the measured yield strength and tensile strength of steel shall not be greater than 0.85. Steel should have obvious yield terrace, and the elongation should be greater than 20%.

2.3.5	Durability requirements of concrete structure:

Environmental category of concrete structure: Category V environment for basement exterior wall and floor below 0.00, and Category 2A environment for others; Outdoor members such as roof, kitchen, toilet and balcony above 0.00: Category 2A environment, Category I environment for others.

2.4	Service Load of Various Rooms and Floors

2.0 kN/m2 for office, clinic and ward; 2.5 kN/m2 for walkway; 3.5 kN/m2 for stairs; 7 kN/m2 for elevator machine room; 2.0 kN/m2 for accessible roof; 0.5 kN/m2 for non-accessible roof.

2.5	Engineering Geological Conditions and Foundation Selection of the Site (recheck after detailed investigation)

Foundation Scheme: According to the site survey, the sites where the two projects are located are of original landform, and the site soil is sedimentary undisturbed soil without disturbance. Therefore, the natural foundation is temporarily adopted and reinforced concrete independent column foundation is adopted.

2.6	Type Selection of Structures

For the time being, cast-in-situ concrete frame structure is proposed, and cast-in-situ beam-slab structure is adopted for the floor.

3.	Design Description of Water Supply and Drainage

3.1	Design Scope

The Project is equipped with water supply system, hot water system, drainage system, indoor and outdoor fire hydrant system and building fire extinguisher.

3.2	Water Supply System

3.2.1	The Max. water consumption of the Project is 15 m3/d; the water drainage is 13.5 m3/d.

3.2.2	In the Project, DN80 municipal water supply pipes are introduced from the surrounding municipal water supply pipe network as water sources for living and fire fighting. The pressure of municipal water supply is calculated by 2.5MPa.

3.2.3	Cold water is directly supplied by municipal water supply and roof water tank, with water tank capacity of 15 m3.

3.2.4	Bottled purified water will be used as drinking water.

3.2.5	Natural gas is used as the heat source of domestic hot water. The heat consumption of domestic hot water is 44kW. Two 22kW gas water heaters are used for central heating.

3.3	Drainage System

3.3.1	The single stack drainage with the stack vent shall be adopted for the indoor sewage. After being treated in outdoor oil separator, the kitchen wastewater shall be discharged into the outdoor sewage pipe network of the hospital. The hospital sewage and wastewater shall be discharged into the outdoor septic tank and the underground sewage treatment station of the hospital, and then shall be discharged into the municipal sewage pipe network after the centralized disinfection treatment.

3.3.2	The roof rainwater shall be discharged to the outside through the organized drainage. The outdoor rainwater shall be discharged to the ditch at the low road side nearby.

3.4	Fire Protection

3.4.1	The effective volume of a proposed fire water tank of the Project is 252 m3. The firefighting pump house shall be provided with one indoor fire pump and one outdoor fire pump. One high-level fire water tank with the effective volume of 18 m3 shall be set at the highest part of the roof.

3.4.2	The outdoor firefighting flow is 25 L/S, with the fire duration of 2 hours.

3.4.3	Each individual building shall be provided with the indoor fire hydrant system, with the firefighting flow of 10 L/S and the fire duration of 2 hours.

3.4.4	The portable dry powder fire extinguisher shall be arranged in the public area indoors. The extinguishing agent is ammonium phosphate.

4.	Design Description of HVAC Discipline

4.1	Design Scope

Design for cold and heat sources, heating, air conditioners, ventilation and smoke prevention and exhaust

4.2	Heating and Air-conditioning Systems

4.2.1	The gas-fired hot water boiler shall be adopted for the heating through the plate-type exchanger in winter. The cylinder-type steel radiator shall be set indoors for the heating, with the heat load of 240kw. Two gas-fired hot water boilers with the heat load of 180kw shall be adopted.

4.2.2	The split air conditioner shall be adopted for the cooling, with the split wall-mounted air conditioner or the split vertical air conditioner.

4.3	Ventilation System

4.3.1	The natural ventilation shall be adopted for the room with exterior windows.

4.3.2	The smoke purifier shall be set on the fume exhaust pipe of the kitchen in the canteen, and the smoke can be purified and then be discharged to the outside through the mechanical ventilation. The peacetime ventilation and the emergency ventilation shall be provided as well.

4.3.3	The mechanical ventilation shall be adopted for the boiler room. The peacetime ventilation and the emergency ventilation shall be provided.

4.3.4	The mechanical ventilation shall be adopted for equipment rooms such as the distribution room and the water pump room.

4.4	Smoke Prevention and Exhaust and Fire Protection Measures

4.4.1	The natural smoke exhaust shall be adopted for all rooms that meet natural smoke exhaust conditions.

4.4.2	The natural smoke exhaust shall be adopted for all enclosed staircases that meet natural smoke exhaust.

4.4.3	The mechanical smoke exhaust system shall be set in the corridor in the ward building.

4.5	Design of Gas System

The natural gas from the municipal external network shall be introduced into the pressure regulating station and shall be regulated to 0.2Mpa; and then shall be connected to the kitchen equipment, the gas-fired hot water boiler and the gas-fired water heater. The total gas consumption of the Project is 35 m3/h.

4.6	Environmental Protection Measures

4.6.1	The environmental equipment and materials compliant with local requirements shall be adopted for the Project.

4.6.2	Environment-friendly refrigerants (such as R134a and R410a) shall be adopted for split air conditioners so as to reduce the impact on the environment.

4.6.3	The sewage and wastewater shall be treated by the septic tank and be disinfected. The kitchen wastewater shall be treated by the grease trap before being discharged into municipal water drainage pipes.

5.	Design Description of Electrical Discipline

5.1	Design Scope

LV: the power supply and distribution system, the power distribution system, the lighting distribution system and the lightning protection and grounding protection system

ELV: the generic cabling system, the cable television system, the video monitoring system, the public address and fire emergency broadcast system, the automatic fire alarm and fire coordinated control system, the entrance and exit management system and the medical information system.

5.2	Power Supply and Distribution System

5.2.1	Load class: The power supply for fire fighting, the security and the medical equipment and the communication power with power off time requirements shall be Class II load; others shall be Class III load.

5.2.2	The one-circuit municipal medium voltage line (10KV) shall be adopted for the power supply. One transformer shall be set by Grenada. The low-voltage distribution shall be 400/230V with the power frequency of 50Hz.

One diesel generator set shall be provided as the backup power supply by China. All load electricity shall be considered based on requirements of Grenada.

5.2.3	The low-voltage metering shall be adopted for the power supply, and the reactive compensation shall be the compensation at the low voltage side.

5.3	Power Distribution System

The radial power supply shall be adopted for the power load; the combined radial and trunk power supply shall be adopted for other power equipment.

5.4	Lighting System

5.4.1	Lamps and light source: According to requirements of different functional rooms, corresponding lamps and light sources shall be configured, and tricolor fluorescent lamps shall be mainly adopted.

5.4.2	Sockets provided by the non-Chinese party shall be in accordance with the local European Standard.

5.5	Lightning Protection and Grounding System

5.5.1	Buildings in the Project shall be the Class III lightning protection buildings. Measures for the direct lightning strike protection, the lightning electromagnetic pulse protection and the lightning induction prevention shall be taken, and the common grounding protection system shall be adopted.

5.5.2	The TN-C-S system and the three-phase four-line grounding system shall be adopted for the Project. Inlet wires of all buildings shall be grounded repeatedly, and PE and N wires shall be separated strictly.

5.6	Generic Cabling System

5.6.1	Grenada shall be responsible for connecting telephone and network cables and optical fibers required for the Project to the telecommunications room. The transmission of the voice, the data and the multi-media can be supported by the generic cabling system.

5.6.2	Optical fibers or multi-pair unshielded twisted-pair cables shall be adopted for the signal transmission. CAT6 double-hole standard RJ45 information sockets shall be used.

5.7	Cable Television System

5.7.1	TV signals shall be introduced by Grenada, and the front-end equipment shall be set in the receiving room to process and magnify TV signals.

5.7.2	The distribution-branch equipment shall be arranged properly. Low-loss coaxial cables shall be adopted for transmission lines, and TV sockets shall be set at terminals.

5.8	Video Monitoring System

5.8.1	The surveillance camera shall be set at the main entrance, and monitoring contents shall be transmitted to the main engine of the monitoring room through video cables. The digital monitoring system shall be adopted for the security monitoring.

5.8.2	The bus and camera integrated system shall be used. The system consists of the digital hard-disk video recorder host, the control keyboard and the monitor.

5.9	Public Address and Fire Emergency Broadcast System

Loudspeakers shall be installed in the corridor and other positions where necessary. The broadcasting host shall be set in the fire-fighting room with the full-digital broadcasting, and it shall be forcibly switched to the fire emergency broadcasting in case of fire.

5.10	Automatic Fire Alarm and Fire Coordinated Control System

5.10.1	The concentrated alarm system shall be adopted for the Project. The fire alarm controller and the fire linkage controller with centralized control functions shall be set in the fire control room.

5.10.2	The bus fire-fighting system shall be adopted. The overall protection shall be adopted. The smoke detector and the heat detector shall be set at locations required by specifications. Manual fire alarm buttons and fire telephone jacks shall be installed at main entrance and exit.

5.11	Entrance and Exit Management System

Access control points shall be set at key entrance and exit, and passages for patients and doctors so as to verify and record identities of entrants.

5.12	Medical Information System

The medical information system shall be set in the lobby and the elevator hall so as to provide fast, abundant and real-time public information and display the bulletin information.